## Slide 1: Circuit Breakers and Measuring Transformers
- Deshmukh Anand Rao (Rtd. GM)

## Slide 2: Substation
Types of substations
Outdoor
Indoor
  Air Insulated
  Gas Insulated
  Hybrid
  Circuit breakers are most important and critical equipment in any sub station

## Slide 3: Circuit Breaker
Plays most critical role in electrical system
Capable of making, carrying and breaking currents under normal conditions
Also capable of making, carrying for a specifies time and breaking currents under abnormal conditions
It consists of control circuit, operating mechanism and Interrupter
Protective relays work like human brain and receives inputs from instrument transformer(sense organs) and other operator’s requirement and finally gives commands to closing and tripping coils
During separation of contacts high currents medium around contacts gets ionized forming an arc
Arc depends on potential difference, ionized particle, operating time and quenching medium

## Slide 4: Circuit Breaker
Types of circuit breakers
Air circuit breaker
Air blast circuit breaker (High pressure H2, N2 or CO2 is used for quenching arc)
Oil Circuit breaker
  Bulk oil circuit breaker
  Minimum oil circuit breaker
VCB
SF6

## Slide 5: Circuit Breaker
Specifications
Voltage rating
Current rating
Short time current rating (3 sec) (KA) rms
Rated 1 min power frequency voltage
Rated peak withstand current (KAp)
Rated making current (KAp)
Breaking current - (KArms)
Operating mechanisms
  Motorised spring operation
  Manual spring charging
Closing and tripping coil (DC)
Manual provision for closing and tripping
  Local Indications
  Close Indication
  Trip Indication
  Spring charge
  Test position
  Service position
  Racked out position
  Counter

## Slide 6: Circuit Breaker
Type | Advantages | Disadvantages
Oil CB | Good dielectric strength Low Cost | Takes more cycles for arc quenching Highly inflammable, risk of fire High maintenance
Vacuum CB | Very low arc Low fire hazard Low maintenance cost Simple mechanism | High initial cost
SF6 | Very short arching time Can interrupt very high currents Less fire risk | Slightly costly
Air Blast CB | High Speed Operation than OCB Less Maint. than OCB Ability to withstand frequent operation | Little moisture content prolongs arcing time Pressure to be monitored closely

## Slide 7: Circuit Breakers
Comparison between VCB and SF6-CB
 | VCB | SF6
Voltage Range | Upto 33 KV | 11-800 KV
Pressure | 10.2 - 10.6 Torr | 1500 - 1875 Torr
Arc Quenching | Low | Slightly High
Suitability | Indoor | Indoor / Outdoor
Maintenance | Rare Maintenance | Periodical Maintenance
Installation | Easy | Difficult
Cost | Low | Slightly high
Application | Medium voltages | All voltages

## Slide 8: Circuit Breaker
Recovery Voltage. :- The RMS voltage that appears across the CB contacts after final Arc interruption( when breaker opens)
Re-striking Voltage :- Voltage at instant of Arc extinction.
Arc Voltage:- During arcing period, when the current flow is maintained in the form of arc.

## Slide 9: Circuit Breaker Maintenance
Tests
Minimum pickup test to check lowest voltage required for coils pickup
Contact resistance Test- Micro Ohm meter
Breaker Timings to check the making and breaking times
Dynamic contact Resistance Measurement(DRM) to check the resistance while contacts are operating

## Slide 10: Circuit Breaker Maintenance
Precautions
Always work on deenergized conditions
Ensure spring is discharged
Only skilled persons should be allowed to work
Instruction manual
Ensure all safety norms are fulfilled
Ensure no mechanical or electrical interlocks are bypassed

## Slide 11: Circuit Breaker Maintenance
Control circuit - Important Safety Features
Trip circuit supervision
Anti pumping
Mechanical and electrical interlocks
Closing From local (Operation Risks)

## Slide 12: Instrument transformers
Current transformer
Principle function is to produce a proportional current at low level in secondary winding which is suitable for operation of low range measuring and protective device like meters and relays
It is a step-up transformer
Important Specifications to be considered:
  Rated Secondary Current
  Rated extended current rating
  Accuracy class
  Accuracy limit factor (ALF)
  Instrument safety factor (ISF)
  Knee point voltage.

## Slide 13
Current transformer
Rated Secondary Current:
  Generally rated secondary currents are 1 Amp or 5 Amps. 1 Amp is preferred to reduce I2R losses which is additional burden on CT core
Rated extended current rating
  Temperature rise shall not increase under extended abnormal conditions. As per IEC-61869-2 120% / 150% / 200%
Accuracy class
  Metering - 0.2 or 0.5 (Less class means more accurate) - Used for revenue/tariff purpose
  Protection - 5P / 10P
  Generally, 2 cores for metering and 5 cores for protections are preferred

## Slide 14
Accuracy limit factor (ALF)
  When system is subjected to fault currents, CT should not saturate. Eg: 5P10 - 10X (Rated Current) /10P30 - 30X (Rated Current)
Instrument safety factor (ISF)
  When system is subjected to fault currents, CT should saturate as meters are not meant for high currents.
      Eg: ISF<5, means saturation should take place at 5 X (Rated Current)
  Saturation will help to protect the meters
5P20 15VA can be read as:
  5 —> Composite error allowed (Is - Ip) X (Kn) (where Kn —> Ip/Is)/ simply +/- 5%
  P —> Protection core
  20 —> Accuracy limit factor (20 X (Rated Current) CT will not saturate)
  15VA —> Burden on CT
  Knee point Voltage-is for 10% voltage rise will result in 50% current increase.
Current transformer

## Slide 15
Importance of CT Secondary short-circuiting (CT Secondary Open):
Secondary current is zero while the primary current remains same.
No opposing flux in secondary
Net flux due to primary current which is very large will lead to saturation
Large flux produces high-voltage which is dangerous to human and instrumentation
Current transformer

## Slide 16: Instrument transformers(CVT and PTs)
Difference Between CVT and PT
S.No | CVT | PT
1 | It consists of both Voltage Capacitance divided and step down transformer. | It is low rated step down transformer with required no.of cores
2 | Low insulation is required because of the presence of capacitences. | High insulation required as it is subjected to direct line voltage
3 | Cheaper because of less insulation | Costlier because of high insulation
4 | Used in carrier communication | Con’t be used
5 | Used for high voltages (>66KV) | Used in low voltages(<66KV)

## Slide 17: Instrument transformers
Voltage transformer
CVT (Capacitive Voltage Transformer):
It can be considered as step-down transformer with capacitance divider
Due to high capacitances it works as high pass filter(Inversely proportional to frequency) This will also facilitate for power line carrier communication
Capacitances 4400 PF / 6600 PF / 8800 PF are kept in series
Equivalent capacitance = (C1 X C2) / (C1 + C2)

## Slide 18
Voltage transformer
Voltage Factor:
Single-phase equipment
During imbalance VT will have different voltages
1.2 continuous
1.5 for 30 seconds
Accuracy Class:
  Metering core - 0.2 / 0.5
  Protection core - 5P / 6P
Thermal burden:
  It is taken considering all windings put together
Simultaneous burden:
  Burden on all windings if not increasing more than the burden mentioned on name plate the accuracy is not disturbed.

## Slide 19
THANK YOU