## Slide 1: Erection, Testing and Commissioning of 132kv CBs in EHT Sub-stations
By
B KameswaraRao
Executive Engineer
MRT & Tr Division, Srikakulam

## Slide 2
The following documents should be ensured before erection and commissioning of Circuit Breakers.
1) Dispatch/delivery documents i.e. Packing list.
2) Instruction manual for operation and maintenance
3) Outline general arrangement, layout and foundation drawing.
4) Schematic and wiring diagrams.
5) Physical checks for any damages to the equipment should be made.

## Slide 3
Erection process:
1) Circuit Breaker foundation:
The circuit breaker foundation should be made as per drawings and the
foundation bolts should be fixed as per template. Threaded portion of
foundation bolts should be left above the concrete level. After curing of
foundation Circuit Breaker erection should be initiated.

## Slide 4
2) For erection of 132kv Circuit Breakers:
a) Keep the required tools available at work spot for erection of CB.
b) Keep SF6 cylinders ready available which were supplied along with CB
c) Keep all bolt & nuts and other accessories available at work spot which were supplied
along with CB.
d) Based on the site conditions, 8T or 12T hydraulic crane can be engaged for erection
of 132kv CBs.
e) Shift the CB mechanism, support structures and poles from stacking yard to work
location.

## Slide 5
f) Clean all the CB parts includes poles, Mechanism box and support
structures perfectly. Open the mechanism box door and remove the moisture
absorbent packs if any.
g) The poles will be supplied with minimum SF6 gas pressure (≤ 1 kg/sq.cm).
Hence ensure the pressure in all poles.
h) Assemble the CB support structures and CB mechanism box on ground. Make
sure that all bolt and nuts tightened perfectly.
i) Lift the total assembled mechanism & structures with crane and position it on CB
foundation. Fix the foundation bolt nuts perfectly duly observing the alignment of
CB. Check water levels in all directions and mechanism should be up to water
level.

## Slide 6
j) Erect the Y-ph pole first on pole base mechanism. Then erect remaining poles.
Note: Fix the “Pole base support clamp” supplied my the manufacturer (CGL) at
the bottom of pole while lifting the pole from horizontal position to
vertical position to avoid damage to bottom pull rod and SF6 inlet adaptor
of pole. Then remove the “Pole base support clamp” before placing on
mechanism.
k) Connect the mechanism linkages to all poles with proper lubricant supplied by
the manufacturer.
l) Connect the SF6 gas pipe linkages to all poles with proper O-ring and gasket
maker supplied by the manufacturer. While connecting the gas pipe linkages
observe the gas pressure gauge inside the mechanism box for proper deflection.
m) Connect the SF6 gas cylinder supplied by the manufacturer at the gas inlet
adopter inside mechanism box through proper regulator and hose pipe and start
filling gas slowly up to 50% of rated pressure.

## Slide 7
n) Check for gas leakages at all pipe line joints.
o) Check “general lockout” and “low SF6 alarm” contacts which should be in close
condition.
p) Continue gas filling up to “general lockout” pressure rating, then check the
“general lockout” contact, it should open.
q) Continue gas filling up to “low SF6 alarm” pressure rating, then check the “low
SF6 alarm” contact, it should open.
r) Continue gas filling up to rated pressure of CB and check for any gas leakages.
s) After filling of SF6 gas, close the gas inlet adopter with cap perfectly.
t) Mechanical ON/OFF operations can be checked.

## Slide 8
3) The following pre-commissioning tests/checks shall be
conducted:
a) Phase to earth, Between phases, across contacts with breaker open to be measured.
The testing should be done with 5KV Megger at below 50% humidity and the
minimum IR value is 100 MΩ for new 132kv CB.
b) Purity and dew point measurement of SF6 gas at rated pressure of the breaker to be
tested. The dew point of SF6 gas should be around - 60 degrees.
c) Measurement of CB close, open, close-open, timings with CB operation analyser.
Opening time : 20-40 m sec
Close time : 60-100 m sec
Close-Open time: below 50 m sec
Note: The maximum time difference between each phase of the circuit breaker during opening and closing operations should not be more than 5ms.

## Slide 9
d) Measurement of Dynamic contact Resistance and contact travel.
The contact resistance should be less than 50 micro- ohm at 20º ambient temperature. It should be around 20 micro-ohms at normal ambient temperature.
e) Measurement of resistance and current drawn by close coil and trip coils I and II.
These values should be as per the designer specification.
f) Checking of operation counter and all mechanical indications.
g) Complete the cable wiring between CB and C&R panel.
h) Extend AC/DC supplies to the circuit breaker

## Slide 10
i) Check auto spring charge operation.
j) Check breaker Open/Close operations in local and from remote.
k) Check CB operational lockouts by simulating the “Low SF6 Alarm” and “General lockout” functions.
l) Check for capacitor tripping function of CB.
m) Now the CB is ready for commissioning.
.

## Slide 11: Thank you one and all
By
B KameswaraRao
Executive Engineer
MRT & Tr Division, Srikakulam