## Slide 1: MRT&Tr -Vijayawada BY T Sreemannarayana Murthy EE/MRT&T/Vijayawada

## Slide 2: 220kv Substatons in Krishna District
Substatons in Krishna District
1.Gunadala 220Kv ss
2.Gudivada 220kv ss
3.Nunna 220kv ss
4.Chillakallu 220kv ss
5.Kondapalli 220kv ss
6.Nuzvid 220kv ss
7.A Konduru220kv ss

## Slide 3: 132 kv substations
1.Auto Nagar 2.Vijayawada
3.Bhavanipuram 4.Konumolu
5.Rangannagudem 6.Kambhampadu
7.Chigurukota 8.Avanigadda
9.Pamarru 10.Machilipatnam
11.Ganguru 12.Nandigama
13 Narasapuram

## Slide 4: UPcoming sub-stations
220kv Tiruvuru ( in construction stage)
132kv Mylavaram( in construction stage)
132kv Vuyyuru
132kv Ramanakkapet
132kv Buntumilli

## Slide 5: Gunadala 220kv substation

## Slide 6: Gudivada 220kv substation

## Slide 7: Nunna 220 kv substation

## Slide 8: Nuzvid 220 substaion

## Slide 9: Kondapalli 220 substation

## Slide 10: Chillakallu 220 substation

## Slide 11: CPDCL network map

## Slide 12: 220kv Gunadala Substation
S.No | Capacity | Total taps/Tap position | make | YOM | DOC | %Impedance | Remarks
1 | 100MVA 220/132kv | 25/23 | Alstom | 2005 | 15/8/2005 | 9.65 | 
2 | 100MVA 220/132kv | 25/23 | CGL | 1995 | 19/11/2014 | 1023 | 
3 | 160MVA 220/132kv | 25/23 | Toshiba | 2015 |  | 9.41 | 
4 | 80MVA /132/33kv | 25/5 | Aditya | 2016 | 24/03/2018 | 11.64 | 
5 | 50MVA 132/33kv | 25/5 | CGL | 2004 | 08/09/2004 | 12.34 | 
6 | 50MVA 132/33kv | 25/5 | Vijai Elec | 2009 | 15/05/2009 | 12.33 | 

## Slide 13: 220kv Gudivada Substation
S.No | Capacity | Total taps/Tap position | make | YOM | DOC | %Impedance | Remarks
1 | 160MVA 220/132kv | 22 | BBL | 2019 | 08/01/2020 | 10.26 | 
2 | 100MVA 220/132kv | 22 | CGL | 2005 | 28/12/2005 | 10.60 | 
3 | 160MVA 220/132kv | 19 | Toshiba | 2015 | 22/11/2017 | 9.14 | 
4 | 50MVA 132/33kv | 5 | BBL | 2019 | 29/09/2019 | 12.50 | 
5 | 50MVA 132/33kv | 5 | Toshiba | 2015 | 15/12/2015 | 11.94 | 
6 | 50MVA 132/33kv | 5 | ECE |  | 31/5/2021 |  | 

## Slide 14: 220kv Konadapalli Substation
S.No | Capacity | Total taps/Tap position | make | YOM | DOC | %Impedance | Remarks
1 | 160MVA 220/132kv | 21/ | BBL | 2019 | 07/01/2020 | 10.30 | 
2 | 100MVA 220/132kv | 25/ | BHEL | 2014 | 10/03/2015 | 10.00 | 
3 | 160MVA 220/132kv | 25/ | Toshiba | 2015 | 23/04/2016 | 9.40 | 
4 | 50MVA 132/33kv | 21/ | BBL | 2016 | 12/01/2017 | 12.47 | 
5 | 31.5MVA 132/33kv | 25/ | EMCO | 1997 | 13/12/2012 | 8.27 | 
6 | 31.5MVA 132/33kv | 25/ | BBL | 2012 | 27/04/2013 | 11.78 | 

## Slide 15: 220kv Nunna Substation
S.No | Capacity | Total taps/ Tap position | make | YOM | DOC | %Impedance | Remarks
1 | 100MVA 220/132kv | 25/ | CGL | 1980 | 07/03/2015 | 9.80 | 
2 | 100MVA 220/132kv | 15/ | BHEL | 2013 | 08/09/2016 | 12.00 | 
3 | 31.5MVA 132/33kv | 25/ | BHEL | 1968 | 15/04/2011 | 12.80 | 
4 | 50MVA 132/33kv | 25/ | T&R | 2012 | 06/12/2012 | 11.82 | 
5 | 31.5MVA 132/33kv | 25/ | Aditya vidyut app | 2017 | 12/04/2018 | 12.08 | 

## Slide 16: 220kv Chillakallu Substation
S.No | Capacity | Total taps/ Tap position | make | YOM | DOC | %Impedance | Remarks
1 | 100MVA 220/132kv |  | BHEL | 1995 | 12/03/1997 | 10.69 | 
2 | 100MVA 220/132kv |  | TELK | 2000 | 14/12/2000 | 11.71 | 
3 | 100MVA 220/132kv |  | Vijai Elec | 2009 | 17/02/2010 | 9.84 | 
4 | 31.5MVA 132/33kv |  | APEX | 1990 | 07/05/1991 | 12.72 | 
5 | 31.5MVA 132/33kv |  | TAL | 2008 | 28/112015 | 12.33 | 
6 | 10/16MVA 132/33kv |  | Indotech |  | 21/12/2020 |  | 

## Slide 17: 220kv Nuzvid Substation
S.No | Capacity | Total taps/Tap position | make | YOM | DOC | %Impedance | Remarks
1 | 100MVA 220/132kv | 25/ | BBL | 2016 | 20/09/2018 | 9.937 | 
2 | 100MVA 220/132kv | 25/ | BBL | 2016 | 20/09/2018 | 9.906 | 
3 | 160MVA 220/132kv | 25/ | BBL | 2019 | 25/07/2020 | 11.91 | 
4 | 50MVA 132/33kv | 25/ | Bharat Bijilee | 2007 | 30/01/2012 | 9.13 | 
5 | 50MVA 132/33kv | 25/ | TELK | 2004 | 28/11/2004 | 13.58 | 
6 | 50MVA 132/33kv | 25/ | BBL | 2011 |  | 6.85 | 
7 | 50MVA 132/33kv | 25 | ECE |  |  |  | 

## Slide 18: PTRs in 132/33KV substations
S.No | Name of 132KV substation | Capacity | Total taps/Tap position | make | YOM | DOC | %Impedance | Remarks
1 | Vijayawada | 50MVA | 25/ | Vijai Elec. | 2010 | 29/03/2013 | 12.12 | 
 |  | 50MVA | 25/ | BHEL | 1984 | 14/07/2010 | 12.58 | 
 |  | 50MVA | 25/ | ECE | 2020 | 31/12/2020 |  | 
2 | Auto Nagar | 50MVA | 25/ | Toshiba | 2018 |  | 12.50 | 
 |  | 50MVA | 25 | Toshiba | 2016 | 14/05/2016 | 12.50 | 
3 | Bhavanipuram | 31.5MVA | 25/ | Andrewyule | 2003 | 31/07/2016 | 11.46 | 
 |  | 31.5MVA | 25/ | EMCO | 1999 | 11/08/2016 | 13.15 | 

## Slide 19: PTRs in 132/33KV substations
S.No | Name of 132KV substation | Capacity | Total taps/Tap position | make | YOM | DOC | %Impedance | Remarks
4 | Konumolu | 50MVA | 25/ | Toshib | 2018 | 23/07/2018 | 12.50 | 
 |  | 31.5MVA | 25/ | APEX | 2000 | 14/06/2012 | 13.09 | 
 |  | 50MVA | 25/ |  | 2020 |  |  | 
5 | Ganguru | 31.5 MVA | 25/ | BBL | 2016 |  | 12.50 | 
 |  | 50MVA | 25 | Toshiba | 2016 | 14/05/2016 | 12.50 | 
6 | Pamarru | 50MVA | 25/ | Toshiba | 2015 | 02/08/2015 | 12.50 | 
 |  | 50MVA | 25/ | Toshiba | 2015 | 11/08/2016 | 12.50 | 

## Slide 20: PTRs in 132/33KV substations
S.No | Name of 132KV substation | Capacity | Total taps/Tap position | make | YOM | DOC | %Impedance | Remarks
7 | Machilipatnam | 50MVA | 25/ | Toshiba | 2018 | 05/06/2018 | 12.50 | 
 |  | 50MVA | 25/ | BBL | 2019 | 23/10/2019 | 12.50 | 
 |  | 50MVA | 25 | ECE |  |  |  | 
8 | Chigurukota | 50MVA | 25/ | Toshiba | 2016 | 18/07/2017 | 11.94 | 
 |  | 31.5MVA | 25 | GEC | 2018 | 21/07/2018 | 12.50 | 
9 | Avanigadda | 31.5MVA | 25/ | BBL | 1994 | 08/08/2016 | 12.37 | 
 |  | 31.5MVA | 25/ | BBL | 2004 | 31/03/2010 | 13.27 | 

## Slide 21: PTRs in 132/33KV substations
S.No | Name of 132KV substation | Capacity | Total taps/Tap position | make | YOM | DOC | %Impedance | Remarks
10 | Nandigama | 50MVA | 25/ | Toshiba | 2018 | 05/06/2018 | 12.50 | 
 |  | 50MVA | 25/ | BBL | 2019 | 23/10/2019 | 12.50 | 
11 | Rangannagudem | 50MVA | 25/ | Toshiba | 2016 | 18/07/2017 | 11.94 | 
 |  | 31.5MVA | 25 | GEC | 2018 | 21/07/2018 | 12.50 | 
12 | Kambhampadu | 50MVA | 25/ | Althom | 1999 | 0/08/2016 | 12.37 | 
 |  | 31.5MVA | 25/ | IMP | 2014 | 31/03/2010 | 13.27 | 

## Slide 22
S.No | Name of ss | 160 MVA | 100 MVA | 80 MVA | 50 MVA | 31.5 MVA | 16 MVA | 
1(220KV) | Gunadala | 1 | 2 | 1 | 2 |  |  | 
2 | Guduvada | 2 | 1 |  | 2 |  |  | 
3 | Nunna |  | 2 |  | 1 | 2 |  | 
4 | Konadapally | 2 | 1 |  | 1 | 2 |  | 
5 | Chillakallu |  | 3 |  |  | 2 | 1 | 
6 | Nuzvid | 1 | 2 |  | 4 |  |  | 
7(132KV) | Auto Nagar |  |  |  | 2 |  |  | 
8 | Vijayawada |  |  |  | 3 |  |  | 
9 | Bhavanipuram |  |  |  |  | 2 |  | 
10 | Ganguru |  |  |  | 2 |  |  | 
11 | Konumolu |  |  |  | 2 | 1 |  | 
12 | Pamarru |  |  |  | 2 |  |  | 
13 | Machilipatnam |  |  |  | 2 |  |  | 
14 | Chigurukota |  |  |  | 2 | 1 |  | 
15 | Avanigadda |  |  |  |  | 2 |  | 
16 | Nandigama |  |  |  | 2 |  |  | 
17 | Rangannagudem |  |  |  | 1 | 1 |  | 
18 | Kambhampadu |  |  |  | 1 | 1 |  | 
 | total | 6 | 11 | 1 | 26 | 14 | 1 | 59

## Slide 23: MR T & Transformer testing
Current transformer
Potential transformer
Circuit breaker
Isolator
C&R panels
Bus bar panels
Power transformer
Lighting Arrester

## Slide 24: Current Transformer
CTs are used to step down the currents to a safe and measurable level
Generally currents will be stepped diwn to 1 amp or 5amp
In APTRANSCo substations CT with 1 amp secondary will be used.
CT secondary should Never be open circuited

## Slide 25: Tests on CTS
Insulation resistance tests (pry to earth, pry to sec core-1, pry to sec core-2,core-1 to earth,core-2 to earth,core-1 to core-2)
Ratio test: primary injection test: current injected in primary wdg and measured in secondary wdg
Tan delta and capacitance: Maximum allowable value for new CT s is 0.7%
For old cts it is upto 1.7% allowed

## Slide 26
Thank You