## Slide 1: APTransco
CV Joshi Dy. Executive Engineer
MRT / Nellore
6 / 16 batch – 23 01 2024
120
240

## Slide 2: Panels
120
240

## Slide 3: Panels
120
240

## Slide 4: Numerical relays
120
240

## Slide 5: Advantages of numerical relays
Speed and Accuracy: Numerical relays respond much faster than electro-mechanical relays due to the absence of moving parts. They provide a more accurate response, as they can be programmed to operate at specific values, whereas electro-mechanical relays have a hysteresis band that can cause errors.
Flexibility: Numerical relays offer greater flexibility in terms of adjustment and configuration options. They can be easily reprogrammed to suit different applications, whereas electro-mechanical relays require physical adjustments to change their settings.
Maintenance: Numerical relays require less maintenance than electro-mechanical relays due to the absence of moving parts. They are less prone to wear and tear, which reduces the likelihood of failure and increases reliability.
Cost: Numerical relays are generally more expensive than electro-mechanical relays due to their advanced technology and programming capabilities. However, over time, they can be more cost-effective as they require less maintenance and have a longer lifespan.
Safety to equipment: Numerical relays offer improved safety features compared to electro-mechanical relays. They can provide faster response times in emergency situations, which can help prevent accidents and minimize damage to equipment.
120
240

## Slide 6: Functions in numerical relays
120
240

## Slide 7: Functions in numerical relays
120
240

## Slide 8: 0
120
240

## Slide 9: Current relay
PT Voltage not required to the relay
120
240

## Slide 10: Current relay
PT Voltage not required to the relay
120
240

## Slide 11: Current relay
120
240

## Slide 12: Directional Current relay
120
240

## Slide 13: Selection of Settings
120
240

## Slide 14: Selection of Settings
120
240

## Slide 15: Trip records in Numerical relays
ER – ARGUS 1
120
240

## Slide 16: Measurements in Numerical relays
ABB – REL 670
ALSTOM – P444
120
240

## Slide 17: Burden ratings
Numerical relays
Electro Mechanical relays
120
240

## Slide 18: Electrical circuit
460 Ω
220 V DC
A
B
C
D
S
V AB=
V CD =
+Ve
-ve
0 V
220 V
220 V
0 V
120
240

## Slide 19: Conditions for drawings
NO
NO
NC
NC
1. Auxiliary supplies in OFF
2. Circuit breaker & Isolators are in OPEN
3. All Control contactors in DEENERGISED condition
4. Pneumatic (air) / Hydraulic (fluid) pressure ZERO
5. WITHOUT SF6 gas pressure in limbs
Note: However concerned drawing to be verified.
120
240

## Slide 20: Battery & Charger
VR Ļ0
VY Ļ240
VB Ļ120
N
Common -ve
Boost +ve
1
110
2.23 x 110 = 245.3 V
B
Relays = 48 to 250 V DC
Trip coils = 220 x 70 ~ 120 % =154 V ~264 V
Close coils = 220 x 80 ~ 110 % =176 V ~242 V
2.3 x 110 = 253 V
2.23 x 110 = 245.3 V
Float
+ve
Float healthy
FC
FCBC
120
240

## Slide 21: Name plate of Cell
120
240

## Slide 22: Operations on battery & charger
1. For taking the readings of cells switch OFF the AC input supply
2. For replacement of a Cell switch OFF Battery input switch
3. To keep the battery in BOOST mode keep FLOAT in ON status,
if FCBC is not available
120
240

## Slide 23: Change over of DC supply
Ex. DCDB 1
Battery 1
Q401
Q402
Q1
Q2
Ex. DCDB 2
Q401
Q402
Q2
Battery 2
Q1
S3
BC
S1
S2
CH 1
CH 2
AC
input
DC
Output
AC
input
DC
Output
S1 & S2 CLOSE
S3 OPEN
120
240

## Slide 24: Change over of DC supply arrangement
120
240

## Slide 25: DC Ratings of relays
120
240

## Slide 26: DC Ratings of relays
120
240

## Slide 27: DC Distribution
120
240

## Slide 28: DC Distribution
120
240

## Slide 29: Current flow in circuit
Protection core 5P20
Metering core 0.2S
P1
400 / 1 - 1 A
P2
S2
S1
S2
S1
S2
S1
S2
S1
S2
S1
S2
S1
S2
S1
I
P1
P2
External circuit
Ammeter
Energy meter
Transducer
Relay
120
240

## Slide 30: Metering Circuit
Metering core
Voltage coil
Protection core
5P20
Metering core
0.2S
P1
400 / 1 - 1 A
P2
Metering core
Ammeter
400
400
400
0
D11
D31
D51
D71
E11
E31
E51
E71
S2
S1
S2
S1
S2
S1
Energy meter
PT
M
M
M
L
L
L
R
Y
B
N
Voltage coil
R
Y
B
N
Transducer OP to RTU
1a
1N
1a
1N
1a
1N
D11A
D31A
D51A
D71
33 kV / 110 V
120
240

## Slide 31: Current relay
Protection core 5P20
P1
400 / 1 - 1 A
P2
S2
S1
S2
S1
S2
S1
R
Y
B
Current Relay
C11
C31
C51
C71
10
09
10
09
10
09
EF Relay
10
09
OC Relay
PT Voltage not required to the relay
120
240

## Slide 32: 132 kV feeder protection
Protection core PS
P1
600 / 1 – 1 – 1 A
P2
S2
S1
S2
S1
S2
S1
R
Y
B
I coil
A11
A31
A51
A71
10
9
10
09
V coil
R
PT
Y
B
E11
E31
E51
E71
Distance Protection relay
132 kV / √3 /110 V/ √3
Impedance measurement
120
240

## Slide 33: 132 kV feeder protection
P1
P2
S2
S1
S2
S1
S2
S1
R
Y
B
I coil
C11
C31
C51
C71
10
9
10
09
V coil
R
PT
Y
B
E11
E31
E51
E71
Backup relay
Protection core PS
132 kV / √3 /110 V/ √3
Current measurement
Inverse curve
600 / 1 – 1 – 1 A
120
240

## Slide 34: 220 kV feeder protection
P1
800 / 1 – 1 – 1 – 1 – 1 A
P2
S2
S1
S2
S1
S2
S1
R
Y
B
I coil
A111
A131
A151
A171
10
9
10
09
V coil
R
PT
Y
B
E111
E131
E151
E171
Main 1
Protection core PS
CVT
Impedance measurement
220 kV / √3 /110 V/ √3
120
240

## Slide 35: 220 kV feeder protection
P1
P2
S2
S1
S2
S1
S2
S1
R
Y
B
I coil
A211
A231
A251
A271
10
9
10
09
V coil
R
PT
Y
B
E211
E231
E251
E271
Main 2
Protection core PS
CVT
Impedance measurement
220 kV / √3 /110 V/ √3
800 / 1 – 1 – 1 – 1 – 1 A
120
240

## Slide 36: 220 kV feeder protection
P1
P2
CT
PT 1
Main 2
(220 kV / √3) /(110 / √3 )
CVT
Main 1
B2
B1
PT 2
Selected Bus PT
CVT
(220 kV / √3) /(110 / √3 )
(220 kV / √3) /(110 / √3 )
75B
75A
Stay put relays
Bus PT Selection relays
800 / 1 – 1 – 1 – 1 – 1 A
52
120
240

## Slide 37: 220 kV feeder protection Voltage selection
PT 1
Main 2
=220 kV /110 V
CVT
Main 1
PT 2
Selected Bus PT
CVT
(220 kV / √3) /(110 / √3 )
75B
75A
120
240

## Slide 38: 400 kV Dia arrangement
1
3
B1
2
P1
P1
F1
F2
400 kV
B2
400 kV
P1
P1
401
402
403
CVT 1
CVT
CVT 2
CVT
BC
120
240

## Slide 39: 400 kV Double break breaker
120
240

## Slide 40: 400 kV feeder protection Voltage selection
Main 1
400 kV /110 V
L. CVT
Metering
Selected Bus CVT
CVT
(400 kV / √3) /(110 / √3 )
Main 2
CVT 1
CVT 2
120
240

## Slide 41: Bus PT / CVT Selector switches
120
240

## Slide 42: 400 kV feeders CT wiring
1
3
B1
2
P1
P1
F1
F2
400 kV
B2
400 kV
P1
P1
401
402
403
CVT 1
CVT
CVT2
CVT
P1
P1
Dead Zone
120
240

## Slide 43: 400 kV Line Stub protection
1
3
B1
2
P1
P1
F1
F2
400 kV
B2
400 kV
P1
P1
401
402
403
DPS
CVT
120
240

## Slide 44: 400 kV Line Stub protection
120
240

## Slide 45: 400 kV ICT Stub protection
120
240

## Slide 46: Cores in a CT
Protection core 5P20
Metering core 0.2S
P1
400 / 1 - 1 A
P2
S2
S1
S2
S1
S2
S1
S2
S1
S2
S1
S2
S1
33 kV
132 kV
220 kV
Protection core 5P20
Metering core 0.2S
Protection core PS
Protection core PS
Metering core 0.2S
Protection core PS
Protection core PS
S2
S1
S2
S1
S2
S1
600 / 1 - 1 - 1 A
800 / 1 – 1 - 1 - 1 - 1 A
120
240

## Slide 47: CTs specifications
120
240

## Slide 48: CTs specifications
ISF:
Maximum value of primary current after which the CT core becomes saturaed
5P20 : for OL & EF core
Tolerance +/- 5% upto 20 times the rated current.
PS : Purchaser’s specification
For Distance, Differential, REF & Bus bar protection
It mainly defines knee point voltage of the core pertaining to a specific application.
0.2S : For metering core defines +/- 0.2% tolerance from 20% to 120% of load current
120
240

## Slide 49: Cores in a CT
S2
S1
S2
S1
400 kV
Dist. Prot. M2 PS
Metering core 0.2S
Dist. Prot. M1 PS
BB Protection PS
S2
S1
S2
S1
2000 / 1 – 1 - 1 - 1 - 1 A
1
3
B1
2
P1
P1
F1
F2
400 kV
B2
400 kV
P1
P1
401
402
403
120
240

## Slide 50: 400 kV Bus bar protection operation
1
3
B1
2
P1
P1
F1
F2
400 kV
B2
400 kV
P1
P1
401
402
403
120
240

## Slide 51: Wiring in Marshalling box
Protection core 5P20
P1
400 / 1 - 1 A
P2
S2
S1
S2
S1
S2
S1
R
Y
B
4 Core Copper
2.5 Sq.mm Cable
R1S1
R1S2
Y1S1
Y1S2
B1S1
B1S2
CT Marshalling Box
120
240

## Slide 52: Ferrules
A = Distance / Differential protection CT Circuit
B = Busbar protection CT Circuit
C = Feeder / PTr Over current & EF Circuit
D = Feeder / PTr Metering CT Circuit
E = Potential circuit - PT
H = AC Circuit – Auxiliary supply
J = DC Circuit – Input supply
K = DC Circuit – Control circuit
L = Indication circuit ( L1-L2)
L = Annunciation circuit (L101-L102)
M = Spring Charge Motor control circuit
N = OLTC circuit P = LBB DC circuit
S = DC circuit - SAS
T = Trip leads
U = Auxiliary switch contacts
120
240

## Slide 53: 0
120
240

## Slide 54: Vector sum
1 Ļ0
1 Ļ240
1 Ļ120
90
180
270
90
180
270
Resultant = 0
120
240

## Slide 55: Vector sum
1 Ļ0
1 Ļ240
1 Ļ120
90
180
270
90
180
270
Resultant = 0
Resultant > 0
120
240

## Slide 56: Vector sum
1 Ļ0
1 Ļ240
1 Ļ120
90
180
270
90
180
270
Resultant = 0
Resultant > 0
120
240

## Slide 57: Vector sum
1 Ļ0
1 Ļ240
1 Ļ120
90
180
270
90
180
270
Resultant = 0
Resultant > 0
120
240

## Slide 58: Fixing of Direction
90
180
270
1 Ļ0
1 Ļ240
1 Ļ120
90
180
270
Resultant = 0
I Flt L0
90
180
270
V Flt L180
V
a
n
a
n
a
n
PT
In balanced condition
V = 0 V
120
240

## Slide 59: Fixing of Direction
90
180
270
1 Ļ0
1 Ļ240
1 Ļ120
90
180
270
Resultant = 0
I Flt
90
180
270
V Flt
I Flt
V Flt
V Flt L315
V Ref
180 + 135 = 315
45
225
30
250
180
0
270
L
L
120
240

## Slide 60: Direction of Operation of Directional relays
1
2
6
3
4
5
A
B
C
120
240

## Slide 61: Direction of Operation of Directional relays
1
2
6
3
4
5
A
B
C
7
120
240

## Slide 62: Directional Over current & Directional Earth fault relays
120
240

## Slide 63: 0
120
240

## Slide 64: Philosophy of Numerical distance protection relay
For 132 kV, 220 kV & 400 kV feeders
1200
600
300
0
Z1
Z5R
Z2
Z3
Z4
80 % L
L
Z
mSec
100 % L + 50%SL
Local Bus
33 kV
21
Z1
80 % L
100 % L + 50%SL
Z2
Z3
100 % L + 120%SL
Z4
Z5R
Z2
100 % L + 50%SL
Z3
Z4
300
100 % L +
120%LL(Z.PTrs)
50% SL(LB)
100 % L + 120%SL
100 % L + 120%SL
SL
LL
Remote Bus
120
240

## Slide 65: Philosophy of Numerical distance protection relay
1. Zone 1 – has to protect up to 80 % of line length
  2. Zone 1 – 1 Ph to Ground fault should trip the faulty phase only
  3. After tripping faulty phase it has to RECLOSE after a time delay of 1 Sec
  4. After reclosing RECLAIMING TIME should start – up to 25 Sec
  5. If any trip occurs with in RECLAIMING time it has to issue 3Ph TRIP.
  6. For all Ph – Ph faults 3 Ph TRIP should issue.
For 220 kV & 400 kV feeders
  7. For SWITCH ON TO FAULT ( SOTF ) & TRIP ON RECLOSE ( TOR )
  3 Ph trip has to issue
  8. For OVER VOLTAGE TRIP (110%) 3 Ph trip should issue DIRECT TRIP SEND
  9. For Zone 2 START & Carrier RECEIVE condition (Zcom )1 Ph trip
  should occur with auto reclose of breaker ( it covers after 80 % of line up to 100 % )
120
240

## Slide 66: Philosophy of Numerical distance protection relay
For 220 kV & 400 kV feeders
10. Other than Z1 - 1Ph fault & Z2 –1Ph Zcom trip, ie. Z2, Z3, Z4 &Z5R – 3 Ph trip
11. In 400 kV lines STUB protection to be ENABLED when line isolator is in OPEN
condition
12. Directional Earth fault protection to be enabled as Backup protection
13. When VT Fuse fail condition is enabled Distance protection scheme gets blocked
and D.OC & D.EF elements are inoperative and OC & EF with VT Fail condition
to be ENABLED
14. Broken conductor ALARM to be configured with time delay of 5 Sec.
15. VT Fuse fail ALARM to be asserted with time delay of 5 Sec
120
240

## Slide 67: Relay settings
30 GROUP-1 DISTANCE ELEMENT:
3001 Group-1 line settings
3002 Line Length 167.0 Km
3004 Line Impedance 26.57
3005 Line Angle 81.16 Deg
3007 Zone Status 110110
3008 kZ1 Res Comp 0.81
3009 kZ1 Angle -2.28 Deg
300A Z1 21.25 Ohm
300C R1G 20.88 Ohm
300D R1Ph 8.88 Ohm
300E tZ1 0.00 Sec.
300F kZ2 Res Com 0.81
3010 kZ2 Angle -2.28 Deg
3011 Z2 31.88 Ohm
3012 R2G 25.06 Ohm
3013 R2Ph 10.66 Ohm
3014 tZ2 0.30 Sec.
3015 kZ3/4 Res Comp 0.81
3016 kZ3/4 Angle -2.28 Deg
3017 Z3(used as zone-4) 54.63 Ohm
3018 R3G-R4G 31.33 Ohm
3019 R3Ph-R4Ph 13.33 Ohm
301A tZ3 1.20 Sec.
301B Z4 (Reverse) 5.31 Ohm
301C tZ4 0.50 Sec.
301D Zone P-Direct(used as zone-3) Directional FWD
301E kZp Res Comp 0.81
301F kZp Angle -2.28 Deg
3020 Zp 39.85 Ohm
3021 RpG 28.19 Ohm
3022 RpPh 11.99 Ohm
3023 tZp 0.60 Sec.
3025 kZm Mutual Com 0.72
3026 kZm Angle -1.09 Deg.
SEL 311 C – 132 kV
P444 – 220 kV
120
240

## Slide 68: 0
120
240

## Slide 69: 220 kV Feeder Protection
70 %
Zone 1, B Ph
70 %
Carr. Send
Zone 1, B Ph
30 %
Carr. Send
Carr. RECV
Carr. RECV
AR Success
AR Success
B
A
90 %
Zcom trip = Z2 St.+ CR
B Ph, 90 %
Carr. Send, Carr.Recv
Z1 trip, B Ph
10 %
Carr. Send, Carr.Recv
Z2 time 300 mSec
Relay
Relay
Carr. RECV
Carr. RECV
Carr. Send
Carr. Send
Comm. Panel
Comm. Panel
6 mS
120
240

## Slide 70: DPS test results
3.75
6.85
9.80
16.1
120
240

## Slide 71: Various relays using
SCHWEITZER ELECTRIC LABAORATORIES - SEL 311C
ABB – REL 650, REL 670
GE or Schneider - P442, P444
SIEMENS – 7SA610,
Distance protection relays:
Backup relays: Dir. OL & Dir.EF relays
SIEMENS – 7SJ62, 7SJ66
GE or SCHNEIDER – P126, P127, P141, P14D
ABB – REF615
Bus bar protection
GE - B90 – Centralised BB prot.
ALSTOM – P741 & P743 – Distributed BB Prot.
NR – PCS 915
NR – PCS 902
NR – PCS 9705
120
240

## Slide 72: Protection scheme for feeders
S. No | Voltage level | Protection used | Additional protection
1 | 33 kV | Non Directional OL & EF | NIL
2 | 132 kV | Dist. Protection as Main Dir. OL & D. EF as Back up | NIL
3 | 220 kV | Dist. Protection as Main1 & Main 2 | Over voltage with DT DT for LBB D.EF for high resistance faults with DT D.EF with VT fuse fail with DT
4 | 400 kV | Dist. Protection as Main1 & Main 2 | Over voltage with DT DT for LBB D.EF for high resistance faults with DT D.EF with VT fuse fail with DT STUB
For short lines Differential prot. as main protection and Dist. Protection as BACK UP, without time delay, in Main1 & Main 2 if communication fails
120
240

## Slide 73: Pole discrepancy Protection
+ ve
- ve
Delay
CB is in ON status
PD Trip Contactor
R
Y
B
Timer
52 a
52 b
200 mSec
1500 mSec
120
240

## Slide 74: Numerical Relay
220 V DC
VY
VB
VN
VR
IY
IB
IN
IR
Analog Cards
220 V DC
Digital Cards
Status inputs
+ ve
- ve
+ ve
- ve
+ ve
Outputs
CB R Ph OFF
CB Y Ph OFF
CB B Ph OFF
CB R Ph trip
CB Y Ph trip
CB B Ph trip
CB 3 Ph trip
Relay
Relay
Watch dog
L101
L103
Num. relay faulty
110 V
1 A
120
240

## Slide 75: Numerical Relay BIO
220 V DC
Digital Cards
Status inputs
+ ve
- ve
+ ve
Outputs
CB R Ph OFF
CB Y Ph OFF
CB B Ph OFF
CB R Ph trip
CB Y Ph trip
CB B Ph trip
86 CB 3 Ph trip
52 b
+ ve
NC
Breaker
Relay
- ve
86
+ ve
NO
86
L
Trip coils
120
240

## Slide 76: Numerical Relay
220 V DC
Status inputs
+ ve
- ve
Outputs
Relay
Zone 1 Single ph. trips
Current
CB R, Y, B OPEN Status
Carrier Receive
SOTF Initiation
Zone 2 + Carrier Receive = Zcom trip - Single ph. trips
Voltage
Zone 2 3ph. trips
Zone 3 3ph. trips
Zone 4 3ph. trips
Zone 5 - Reverse 3ph. trips
Carrier send
Line Isolator OPEN
STUB protection OPTD 3 Ph trip (400 kV only )
Dir. EF OPTD
VTF - EF OPTD
VTF – Over Current OPTD
SOTF OPTD 3 Ph trip
Broken conductor Alarm
VT Fuse fail alarm
Power swing alarm
Configuration PSL
120
240

## Slide 77: Feeder Trip matrix
120
240

## Slide 78: 0
120
240

## Slide 79: Improper earthing
120
240

## Slide 80: Improper earthing
120
240

## Slide 81: Improper earthing
1. Delay in tripping
2. Unwanted tripping
3. Flash over of equipment and damage to the
adjacent equipment
4. Most probably fault current enters into battery
through battery earthing system
5. Getting shock when touched the metal parts in
the substation
120
240

## Slide 82: Tan D Measurement
Ic
E
Ic1
Tan D = 0.007 = 0.7%
Tan D > 0.7%
D2 > D1
Constant at all Voltages
C
R
Ic2
D2
R
D1
120
240

## Slide 83: TanD terminal OPEN
120
240

## Slide 84: 0
120
240

## Slide 85: 0 %
Variable transformer
100%
110%
Input
0 – 230 V
AC
Output =
Ph
N
230 V
252 V
V
0
100
200
252
120
240

## Slide 86: Idle charging of transformers
Tap | Fine Selector | Pre selector | Pri. V | Sec V | 50 MVA
1 | 17 | 5-4 | 138600 | 33000 | 208.3
2 | 16 | 5-4 | 136950 | at all taps | 210.8
3 | 15 | 5-4 | 135300 |  | 213.4
4 | 14 | 5-4 | 133650 | 874.8 A | 216.0
5 | 13 | 5-4 | 132000 |  | 218.7
6 | 12 | 5-4 | 130350 |  | 221.5
7 | 11 | 5-4 | 128700 |  | 224.3
8 | 10 | 5-4 | 127050 |  | 227.2
9 | 9 | 5-4 | 125400 |  | 230.2
10 | 8 | 5-4 | 123750 |  | 233.3
11 | 7 | 5-4 | 122100 |  | 236.4
12 | 6 | 5-4 | 120450 |  | 239.7
13a | 5 | 5-4 | 118800 |  | 243.0
13b | 4 | 5-4 / 5-3 | 118800 |  | 243.0
13c | 17 | 5-3 | 118800 |  | 243.0
14 | 16 | 5-3 | 117150 |  | 246.4
15 | 15 | 5-3 | 115500 |  | 249.9
16 | 14 | 5-3 | 113850 |  | 253.6
17 | 13 | 5-3 | 112200 |  | 257.3
18 | 12 | 5-3 | 110550 |  | 261.1
19 | 11 | 5-3 | 108900 |  | 265.1
20 | 10 | 5-3 | 107250 |  | 269.2
21 | 9 | 5-3 | 105600 |  | 273.4
22 | 8 | 5-3 | 103950 |  | 277.7
23 | 7 | 5-3 | 102300 |  | 282.2
24 | 6 | 5-3 | 100650 |  | 286.8
25 | 5 | 5-3 | 99000 |  | 291.6
2U
2N
132 kV / 33 kV
YNyn0
1U
17
3
4
1
4
13a
13b
5
1N
13c
120
240

## Slide 87: Idle charging of transformers
120
240
132 kV / 33 kV
YNyn0
5
1U
2U
1N
17
3
4
1
2N
4
13a
13b
13c
13b
5
13c
13a
Tap | Fine Selector | Pre selector | Pri. V | Sec V | 50 MVA
1 | 17 | 5-4 | 138600 | 33000 | 208.3
2 | 16 | 5-4 | 136950 | at all taps | 210.8
3 | 15 | 5-4 | 135300 |  | 213.4
4 | 14 | 5-4 | 133650 | 874.8 A | 216.0
5 | 13 | 5-4 | 132000 |  | 218.7
6 | 12 | 5-4 | 130350 |  | 221.5
7 | 11 | 5-4 | 128700 |  | 224.3
8 | 10 | 5-4 | 127050 |  | 227.2
9 | 9 | 5-4 | 125400 |  | 230.2
10 | 8 | 5-4 | 123750 |  | 233.3
11 | 7 | 5-4 | 122100 |  | 236.4
12 | 6 | 5-4 | 120450 |  | 239.7
13a | 5 | 5-4 | 118800 |  | 243.0
13b | 4 | 5-4 / 5-3 | 118800 |  | 243.0
13c | 17 | 5-3 | 118800 |  | 243.0
14 | 16 | 5-3 | 117150 |  | 246.4
15 | 15 | 5-3 | 115500 |  | 249.9
16 | 14 | 5-3 | 113850 |  | 253.6
17 | 13 | 5-3 | 112200 |  | 257.3
18 | 12 | 5-3 | 110550 |  | 261.1
19 | 11 | 5-3 | 108900 |  | 265.1
20 | 10 | 5-3 | 107250 |  | 269.2
21 | 9 | 5-3 | 105600 |  | 273.4
22 | 8 | 5-3 | 103950 |  | 277.7
23 | 7 | 5-3 | 102300 |  | 282.2
24 | 6 | 5-3 | 100650 |  | 286.8
25 | 5 | 5-3 | 99000 |  | 291.6
17
15
13
11
9

## Slide 88: 50 MVA, 132 kV / 33 kV
120
240

## Slide 89: OLTC
120
240

## Slide 90: OLTC operation
R
R
R
R
7
8
7
8
120
240

## Slide 91: OLTC
The switching time of a diverter switch is between 40 and 60 ms with today’s designs. during diverter switch operation, transition resistors are inserted, which are loaded for 20–30 ms, i. e. the resistors can be designed for short-term loading.
120
240

## Slide 92: Idle charging of transformers
3
1U
2U
400 kV / 220 kV
1
2
3
4
N
YNa0 D11
400 kV
220 kV
4
12
4
12
13
1
2
120
240
Tap | Pri. kV | Sec kV
1 | 440 | 
2 | 435 | 
3 | 430 | 
4 | 425 | 
5 | 420 | 
6 | 415 | 
7 | 410 | 
8 | 405 | 
9a | 400 | 220
9b | 400 | at all taps
9c | 400 | 
10 | 395 | 
11 | 390 | 
12 | 385 | 
13 | 380 | 
14 | 375 | 
15 | 370 | 
16 | 365 | 
17 | 360 | 

## Slide 93: Parallel operation of transformers
% Z =
400 kV / 220 kV
315 MVA
1
2
3
12.83
12.83
12.50
4
11.54
500 MVA
ABB
TELK
T&R
ABB
88
88
90
155
Load MW
1.Voltage rating should be same
2.Vector group should be same
3. %Z should be nearly equal to each other or equal (sharing is Inversely proportional to %Z)
4. Power rating may vary (sharing is directly proportional to rating)
5. Phase association to be maintained
YNa0 D11
Load values on 19 12 2023 at 2000 Hr
120
240

## Slide 94: Charging of ICTs
120
240

## Slide 95: Load sharing at different taps
Tap No | All 22 |  | PTR 3 =21 |  | PTR 3 =20 | 
PTR No | MW | PF | MW | PF | MW | PF
1 | 54 | 0.99L | 53 | 1 | 53 | 0.98C
2 | 54 | 0.99L | 54 | 1 | 54 | 0.98C
3 | 61 | 1 | 60 | 0.95L | 64 | 0.89L
120
240

## Slide 96: Power Transformer Protection - Electrical
HV
P1
P1
P1
PS
BB.
PS
REF.
PS
Diff.
5P20
OL&EF
0.2S
Met.
PS
Diff.
5P20
OL&EF
0.2S
Met.
PS
REF.
PS
REF.
400 kV
220 kV
PS
BB
120
240

## Slide 97: Power Transformer Protection - Electrical
HV
P1
P1
5P20
OL&EF
5P20
OL&EF
400 kV
220 kV
120
240

## Slide 98: Directional Over current & Directional Earth fault relays
120
240

## Slide 99: Differential Relay
P1
P1
PS
Diff.
PS
Diff.
Diff. Relay
400 kV
220 kV
120
240

## Slide 100: REF relays
HV
P1
PS
REF.
PS
REF.
PS
REF.
P1
P1
400 kV
220 kV
REF Relay
Bushing CTs
120
240

## Slide 101: REF relay
REF Relay
1U
2U
NU
1S1
1S2
1V
2V
NV
1S1
1S2
1W
2W
NW
1S1
1S2
120
240

## Slide 102: REF relay
Restricted Earth Fault Relay
1U
2U
NU
1S1
1S2
1S1
1S2
1S1
1S2
1V
2V
NV
1W
2W
NW
120
240

## Slide 103: REF relay calculations
Consider 400 kV / 220 kV, 315 MVA ICT
LV I FL = 315 M / (√3 * 220 k) = 826 A
Hence CTR to be selected is 1000 / 1 A on HV , IV & N side
20% of LV I FL Extra = 826 + (20% *826) = 991 ~ 1000 A
REF Min. pickup current Set value = 0.02 A
1 = 1000
X = 20 A primary without stabilizing resistor
0.02 = X
120
240

## Slide 104: PTr Trip matrix
120
240

## Slide 105: 315 MVA ICT REF Name plate
REF
Spare
Metering
REF
Spare
REF
Spare
Metering
1U
2U
400 kV
220 kV
1U-1S1
1U-1S2
1U-2S1
1U-2S2
1U-3S1
1U-3S2
2U-1S1
2U-1S2
2U-2S1
2U-2S2
2U-3S1
2U-3S2
NU-1S1
NU-1S2
NU-2S1
NU-2S2
N
Core | CTR | Class
REF | 1000 / 1 | PS
Spare | 1000 / 1 | PS
Metering | 600 / 1 | 0.2
120
240

## Slide 106: PTr 2 Ph Charging
120
240

## Slide 107: PRV Packed
120
240

## Slide 108: 0
120
240

## Slide 109: 500 MVA ICT Taps Voltage & current
120
240

## Slide 110: 500 MVA ICT Name plate
120
240

## Slide 111: 315 MVA ICT Name plate
120
240

## Slide 112: REF circuit in GE panel
120
240

## Slide 113: Metrosils & Stabilizing resistors
120
240

## Slide 114: REF Settings
APPROVED SETTINGS ON
S.No PARTICULARS 500 MVA, 400/220 KV TRANSFORMER-4(NEW)
===========================================================================
1. C.T.Ratio
HV,LV & Neutral SIDE :-
Available : 1600/1 A
Adopted : 1600/1 A
2. Restricted Earth Fault Protection(REF) Settings:-
a) REF Auto Status : HighZ REF
b) Neutal CT Input : TN1,TN2,TN3
c) Auto Is1 Set : 0.02
d) Auto tREF : 0 Sec
e) Stabilising Resistor(Rst) : 3554 Ohms
120
240

## Slide 115: REF relays connection
P1
P1
120
240

## Slide 116: 0
120
240

## Slide 117: Power Transformer Protection - Electrical
120
240

## Slide 118: Diff. Relay Trip Characteristic
120
240

## Slide 119: 132 kV feeder settings
120
240

## Slide 120: P444 Dist. Prot. Relay settings
30 GROUP-1 DISTANCE ELEMENT:
3001 Group-1 line settings
3002 Line Length 167.0 Km
3004 Line Impedance 26.57
3005 Line Angle 81.16 Deg
3007 Zone Status 110110
3008 kZ1 Res Comp 0.81
3009 kZ1 Angle -2.28 Deg
300A Z1 21.25 Ohm
300C R1G 20.88 Ohm
300D R1Ph 8.88 Ohm
300E tZ1 0.00 Sec.
300F kZ2 Res Com 0.81
3010 kZ2 Angle -2.28 Deg
3011 Z2 31.88 Ohm
3012 R2G 25.06 Ohm
3013 R2Ph 10.66 Ohm
3014 tZ2 0.30 Sec.
3015 kZ3/4 Res Comp 0.81
3016 kZ3/4 Angle -2.28 Deg
3017 Z3(used as zone-4) 54.63 Ohm
3018 R3G-R4G 31.33 Ohm
3019 R3Ph-R4Ph 13.33 Ohm
301A tZ3 1.20 Sec.
301B Z4 (Reverse) 5.31 Ohm
301C tZ4 0.50 Sec.
301D Zone P-Direct(used as zone-3) Directional FWD
301E kZp Res Comp 0.81
301F kZp Angle -2.28 Deg
3020 Zp 39.85 Ohm
3021 RpG 28.19 Ohm
3022 RpPh 11.99 Ohm
3023 tZp 0.60 Sec.
3025 kZm Mutual Com 0.72
3026 kZm Angle -1.09 Deg.
120
240

## Slide 121: P643 Differential relay settings
120
240

## Slide 122: Protection protocol to be followed
120
240

## Slide 123: Protection protocol to be followed
120
240

## Slide 124: Protection protocol to be followed
120
240

## Slide 125: Protection protocol to be followed
120
240

## Slide 126: Protection protocol to be followed
120
240

## Slide 127: 0
120
240

## Slide 128: 220 kV Bus bar protection
P1
400 A
P2
P1
400 A
P2
R
P1
400 A
P2
P1
400 A
P2
P1
800 A
P2
0.5 Ļ0
0.5 Ļ0
0.5 Ļ0
1 Ļ180
0.5 Ļ180
F1
F2
F3
S2
S1
S2
S1
F4
F5
F1 = +1
F2 = +0.5
F3 = -0.5
F4 = -0.5
F5 = -0.5
∑ I = 0
S2
S1
S2
S1
S2
S1
S2
S1
S2
S1
87
120
240

## Slide 129: 220 kV Bus bar protection
P1
400 A
P2
P1
400 A
P2
R
P1
400 A
P2
P1
400 A
P2
P1
800 A
P2
-0.5 A
-0.5 A
-0.5 A
+1 A
+0.5 A
F1
F2
F3
S2
S1
S2
S1
F4
F5
120
240

## Slide 130: 220 kV Bus bar protection
F 1
F 2
S1
S2
F 3
S1
S2
F 4
S1
S2
F 5
87 R
1 Ļ180
0.5 Ļ180
0.5 Ļ0
0.5 Ļ0
0.5 Ļ0
I = 0
F 1
F 2
S1
S2
F 3
S1
S2
F 4
S1
S2
F 5
87 Y
1 Ļ180
0.5 Ļ180
0.5 Ļ0
0.5 Ļ0
0.5 Ļ0
I = 0
F 1
F 2
S1
S2
F 3
S1
S2
F 4
S1
S2
F 5
87 B
1 Ļ180
0.5 Ļ180
0.5 Ļ0
0.5 Ļ0
0.5 Ļ0
I = 0
S1
S2
S1
S2
S1
S2
S1
S2
S1
S2
S1
S2
120
240

## Slide 131: 220 kV Bus bar protection
P1
400 A
P2
P1
400 A
P2
R
P1
400 A
P2
P1
400 A
P2
P1
800 A
P2
0.5 Ļ0
0.5 Ļ0
0.5 Ļ0
3 Ļ180
3 Ļ180
F1
F2
F3
S2
S1
S2
S1
4.5 A
F4
F5
120
240

## Slide 132: 220 kV Bus bar protection
P1
P2
P1
P2
R
P1
P2
0.5 Ļ0
0.5 Ļ0
0.5 Ļ0
F3
P1
P2
3 Ļ180
F1
S2
S1
4.5 A
P1
P2
F2
3 Ļ180
F4
F5
120
240

## Slide 133: 220 kV Bus bar protection
F 1
F 2
S1
S2
F 3
S1
S2
F 4
S1
S2
F 5
87 R
1 Ļ180
0.5 Ļ180
0.5 Ļ0
0.5 Ļ0
0.5 Ļ0
I = 0
S2
S1
F 1
S2
S1
F 2
S1
S2
F 3
S1
S2
F 4
S1
S2
F 5
87 Y
1 Ļ180
0.5 Ļ180
0.5 Ļ0
0.5 Ļ0
0.5 Ļ0
I = 0
S2
S1
F 1
S2
S1
F 2
S1
S2
F 3
S1
S2
F 4
S1
S2
F 5
87 B
1 Ļ180
0.5 Ļ180
0.5 Ļ0
0.5 Ļ0
0.5 Ļ0
I = 0
S1
S2
S1
S2
120
240

## Slide 134: 220 kV Bus bar protection
S1
S2
F 1
S1
S2
F 2
S1
S2
F 3
S1
S2
F 4
S1
S2
F 5
87 R
3 Ļ180
3 Ļ180
0.5 Ļ0
0.5 Ļ0
0.5 Ļ0
I fault = 4.5 A
I set = 0.2A
87 R
87 Y
87 B
+ 220 V DC
1-96
2-96
3-96
4-96
- 220 V DC
1-96
2-96
3-96
4-96
120
240

## Slide 135: 220 kV Bus bar protection
P1
P2
P1
P2
3 Ph
P1
P2
F3
P1
P2
F1
S2
S1
P1
P2
F2
F4
F5
S2
S1
120
240

## Slide 136: 220 kV Double Bus bar protection
P1
400 A
P2
R
0.5 Ļ0
F2
S2
S1
P1
P2
0.5 Ļ180
F1
Bus 1
Bus 2
P1
Bus Coupler
CT1
CT2
F1 = +0.5
F2 = -0.5
CT1= -0.5
I BB set = 0.2A Instanteneous
P1
CT1= +0.5
∑ I = 0 A
P1
CT2 = +0.5
P1
CT2 = -0.5
∑ I = 0 A
R
∑ I = 1 A
∑ I = -1 A
S2
S1
120
240

## Slide 137: 220 kV Double Bus bar protection
P1
400 A
P2
P1
400 A
P2
R
0.5 Ļ0
0.5 Ļ0
F3
P1
P2
0.5 Ļ180
F1
S2
S1
5 A
P1
P2
F2
0.5 Ļ180
F4
Bus 1
Bus 2
P1
P1
Bus Coupler
CT1
CT2
120
240

## Slide 138: 220 kV Bus bar protection
P1
P2
P1
P2
R
-0.5 Ļ0
-0.5 Ļ0
F3
P1
P2
+3 Ļ180
F1
S2
S1
5 A
P1
P2
F2
+3 Ļ180
F4
Bus 1
Bus 2
P1
P1
Bus Coupler
CT1
CT2
2.5 A
3A
3A
0.5A
120
240

## Slide 139: 220 kV Bus bar protection
S1
S2
F 1
S1
S2
F 2
S1
S2
F 3
S1
S2
F 4
S1
S2
CT 1
87 R - A
+3A
+3A
-0.5 Ļ0
-0.5 Ļ0
+2.5A
I flt = 5 A
I BB set = 0.2A Instanteneous
B1 / Zone A
S1
S2
CT 2
-2.5 Ļ0
B2 / Zone B
87 R - B
CT Switching in bus bar protection panel
-0.5A
-2.5A
-0.5A
120
240

## Slide 140: 220 kV Bus bar protection
S1
S2
F 1
S1
S2
F 2
S1
S2
F 3
S1
S2
F 4
S1
S2
CT 1
87 Y - A
-0.5 Ļ0
-0.5 Ļ0
B1 / Zone A
S1
S2
CT 2
B2 / Zone B
87 Y - B
CT Switching in bus bar protection panel
-0.5A
-0.5A
+0.5A
+0.5A
I BB set = 0.2A Instanteneous
120
240

## Slide 141: 220 kV Bus bar protection
S1
S2
F 1
S1
S2
F 2
S1
S2
F 3
S1
S2
F 4
S1
S2
CT 1
87 B - A
-0.5 Ļ0
-0.5 Ļ0
B1 / Zone A
S1
S2
CT 2
B2 / Zone B
87 B - B
CT Switching in bus bar protection panel
-0.5A
-0.5A
+0.5A
+0.5A
I BB set = 0.2A Instanteneous
120
240

## Slide 142: 220 kV Bus bar protection
CT Switching in bus bar protection panel
I BB set = 0.2A Instanteneous
120
240

## Slide 143: 220 kV Bus bar protection
87 R - A
1-89A
+ 220 V DC
87 Y - A
87 B - A
87 R - B
87 Y - B
87 B - B
+
1-89B
- 220 V DC
2-89A
2-89B
3-89A
3-96
3-89B
4-89A
4-89B
1-96
2-96
4-96
2-96
4-96
BC-A
BC-B
BC - B
120
240

## Slide 144: 220 kV Bus bar protection
P1
P2
P1
P2
R
-0.5 Ļ0
-0.5 Ļ0
F3
P1
P2
+3 Ļ180
F1
S2
S1
5 A
P1
P2
F2
+3 Ļ180
F4
Bus 1
Bus 2
P1
P1
Bus Coupler
CT1
CT2
2.5 A
3A
3A
0.5A
+0.5 Ļ180
120
240

## Slide 145: Local Breaker Backup protection
LBB Relay should sense a fault current. I LBB > 0.2 A
2. TRIP initiation should be extended from 86 A / 86 B & 1 ph tripping relays
3. It doesn’t check the status of the breaker.
LOGIC :
&
I LBB > 0.2 A
86 A / 86 B
Master trip relay
LBB Optd
Time delay
&
200 mSec
120
240

## Slide 146: Local Breaker Backup protection
F1 LBB Optd
F1
F2
F3
F4
F2 LBB Optd
F3 LBB Optd
F4 LBB Optd
120
240

## Slide 147: Local Breaker Backup protection
87 R - A
1-89A
+ 220 V DC
87 Y - A
87 B - A
87 R - B
87 Y - B
87 B - B
+
1-89B
- 220 V DC
2-89A
2-89B
3-89A
3-96
3-89B
4-89A
4-89B
1-96
2-96
4-96
LBB Optd >200 mSec
+ 220 V DC
P1
BC-A
BC-B
2-96
4-96
BC-B
120
240

## Slide 148
P1
P2
P1
P2
R
-0.5 Ļ0
-5 Ļ0
F3
P1
P2
+3 Ļ180
F1
S2
S1
5 A
P1
P2
F2
+3 Ļ180
F4
Bus 1
Bus 2
P1
P1
Bus Coupler
CT1
CT2
2.5 A
3A
3A
0.5A
+0.5 Ļ180
Local Breaker Backup protection
120
240

## Slide 149: Local Breaker Backup protection
LBB Relay should sense a fault current. I LBB > 0.2 A
2. TRIP initiation should be extended from 86 A / 86 B
3. It doesn’t check the status of the breaker.
LOGIC :
&
I LBB > 0.2 A
86 A / 86 B
Master trip relay
LBB Optd
Time delay
&
Back Trip
ReTrip
100 mSec
200 mSec
200
mSec
50
0
100
120
240

## Slide 150: Local Breaker Backup protection
F1 LBB Retrip
F1-96
F2 LBB Retrip
F3 LBB Retrip
F4 LBB Retrip
100 mSec
F2-96
F3-96
F4-96
120
240

## Slide 151: Local Breaker Backup protection
&
BB Z1 Optd
F1 Bus 1 Selected
F1
1-96
OR
&
BB Z2 Optd
F1 Bus 2 Selected
F1 LBB RE TRIP
100 mSec
LBB Back Trip to Bus 1
LBB Back Trip to Bus 2
200 mSec
OR
200 mSec
OR
120
240

## Slide 152: Local Breaker Backup protection
LBB Back Trip to Bus 1
F1 LBB Back Trip
&
F1 Bus 1 Selected
F2 LBB Back Trip
F2 Bus 1 Selected
F3 LBB Back Trip
F3 Bus 1 Selected
F4 LBB Back Trip
F4 Bus 1 Selected
OR
200 mSec
&
&
&
LBB Back Trip to Bus 2
F1 LBB Back Trip
&
F1 Bus 2 Selected
F2 LBB Back Trip
F2 Bus 2 Selected
F3 LBB Back Trip
F3 Bus 2 Selected
F4 LBB Back Trip
F4 Bus 2 Selected
OR
200 mSec
&
&
&
120
240

## Slide 153: 0
120
240

## Slide 154: Trip Circuit Supervision Relay
5 kΩ
-Ve
220 V DC
Trip Circuit
Healthy
52a
Relay
OL R
Relay
OL Y
Relay
OL B
Relay
EF
Relay
OL R
Relay
OL Y
Relay
OL B
Relay
EF
86
NO
NC
+ Ve
220 V DC
K1
K3
K2
K4
L
L
120
240

## Slide 155: 86 Latch relay
120
240

## Slide 156: Trip Circuit Supervision Relay
5 kΩ
-Ve
220 V DC
Trip Circuit
Healthy
52a
86
52b
95 A
95 B
95 C
95A
95B
95C
L101
L102
Post close & Protection trip
Pre close
Trip Circuit Healthy
95 B
95 A
95 C
+ Ve
220 V DC
Buzzer Circuit
120
240

## Slide 157: Trip Circuit Supervision Relay
95 B
95 A
95 C
95 B
95 A
95 C
1-95
2-95
95 B
95 A
95 C
95 B
95 A
95 C
1-95 R
2-95 R
95 B
95 A
95 C
95 B
95 A
95 C
1-95 Y
2-95 Y
95 B
95 A
95 C
95 B
95 A
95 C
1-95 B
2-95 B
120
240

## Slide 158: 0
120
240

## Slide 159: Testings of CTs
Insulation resistance test
Insulation resistance test | 
Winding to test | Test Voltage
Primary - Body | 10 kV
Primary - Core 1 | 10 kV
Primary - Core 2 | 10 kV
Primary - Core 3 | 10 kV
Core 1 - Body | 500 V
Core 2 - Body | 500 V
Core 3 - Body | 500 V
Core 1- 2 | 500 V
Core 2 - 3 | 500 V
Core 3 - 1 | 500 V
Polarity Test
P1
P2
0
+
_
1.5 / 9V
DC
S1
S2
mA DC
+
-
CT
120
240

## Slide 160: Testings of CTs
Insulation resistance test
Insulation resistance test | 
Winding to test | Test Voltage
Primary - Body | 10 kV
Primary - Core 1 | 10 kV
Primary - Core 2 | 10 kV
Primary - Core 3 | 10 kV
Core 1 - Body | 500 V
Core 2 - Body | 500 V
Core 3 - Body | 500 V
Core 1- 2 | 500 V
Core 2 - 3 | 500 V
Core 3 - 1 | 500 V
Polarity Test
P1
P2
0
+
_
1.5 / 9V
DC
S1
S2
mA DC
+
-
CT
120
240

## Slide 161: Testings CTs
Ratio Test
P1
P2
S1
S2
Burden
A
Primary injectionKit
with Burden
120
240

## Slide 162: Circuit breakers
Insulation resistance test
Insulation resistance test | 
Test voltage = 10 kV | Ohms
Incoming - Earth | 
Outgoing - Earth | 
Incoming - Outgoing | 
Continuity | 
Breaker timing
Timing test mSec | 
Close | 60
Open TC 1 | 30 - 40
Open TC 2 | 30 - 40
Close – Open TC 1 | Between OPEN & CLOSE
Close – Open TC 2 | Between OPEN & CLOSE
Breaker Contact resistance ~ 50 micro Ohms
Capacitor Tripping Device TO BE KEPT IN SERVICE for Breakers connected to TRANSFORMERS
And TO BE DISCONNECTED to breakers connected to FEEDERS
Time difference between Breaker Primary contacts and
auxiliary switch contacts < 3 mSec
120
240

## Slide 163: 0
120
240

## Slide 164: Case studies
S No | Event | Observation / Rectification | DR
1 | 16 MVA PTr tripping on Differential Protection when loads are taken – at 132 kV Udayagiri SS – 2001 yr | LV side secondary winding error | 
2 | For a fault on 132 kV feeder 1, parallel feeder tripping instantaneously – 220 kV Racharalapadu SS | Settings error 21D | DR
3 | Bus bar protection operated for lightning strike on the feeder – 220 kV Nellore SS | 220 kV Breaker limb got discharged due RRRV | DR PPT
4 | For a Single phase fault on line 220 kV feeder 3 Ph trip occurring – 220 kV Nellore SS | TC 2 Cable trouble | 0
5 | For a Single phase fault on 220 kV Podili 2 line, 3 Ph trip occurring – 220 kV Atmakur SS | Pole discrepancy timer relay & trip multiplier coordination mismatch | DR
6 | Sparks in Cable trench, cable identified but not the source – 220 kV Nellore SS | Multiple AC source switches kept in OFF | 0
120
240

## Slide 165: Case studies
S No | Event | Observation / Rectification | DR
7 | Battery completely discharged due to input supply missing- short circuit of incoming supply cable – 132 kV Anantasagaram SS | Trickled charged the battery with external battery charger | 
8 | 3 Ph tripping occurring for a 1 Ph fault on 220 kV Mydukuru – Srisailam line frequently | Inside P444 relay vermin bite observed | 
9 | 3 Ph tripping occurring for a 1 Ph fault on Racharlapadu – Ongole & Racharlapadu - Nellore lines | BB protection Retrip = 50 mSec  100 mSec | DR retrip DR FDR
10 | For 132 kV Renigunta – Tirupathi radial feeder fault - 132 / 33 kV PTr 2 HV EF relay operated and feeder Dir. EF operated at Tirupathi end | PTr 2 HV EF relay setting error | DR 1 DR 2
120
240

## Slide 166: Case studies
S No | Event | Observation / Rectification | DR
11 | 220 kV Bus 2 insulators flashed over – both Bus2 breakers tripped at this end and Bus1 connected breakers tripped at source end – 400 kV Manubolu | +ve lead loose contact for bus coupler breaker trip circuit | 0
12 | 16 MVA PTr tripping on OLTC Buchholtz trip when tap is operated – 132 kV Atmakuru SS | Transient resistor OPEN | 0
13 | Sync permission not getting high at Nellore SS, hence breaker not getting closed – 132 kV Nellore – Manubolu ( LILO work of 132 kV Nellore – Guduru feeder ) | Stringing error at LILO tower | Table
14 | Sync permission not getting high at 132 kV Atmakuru SS | 132 kV Bus PT wiring error | 0
15 | 220 kV Inaparajupalli – Sricement Line Differential relay operated when loads taken on line | Secondary wiring error | 
16 | 31.5 MVA PTr tripped on Differential protection due to inrush currents | Input 140 kV & Normal tap | 
120
240

## Slide 167: Case studies
Synchronization of Lines – Checking Phase association |  |  |  | 
Volts |  | Line CVT voltage |  | 
 |  | R | Y | B
Bus PT Voltage | R | 0 | 110 | 110
 | Y | 110 | 0 | 110
 | B | 110 | 110 | 0
Ph | Bus PT | Line CVT
RN | 63.5 | 63.5
YN | 63.5 | 63.5
BN | 63.5 | 63.5
RY | 110 | 110
YB | 110 | 110
BR | 110 | 110
Bus PT
Line CVT
V
120
240

## Slide 168: Diff. Relay Secondary Wiring
2S1
2S2
2S1
2S2
P1
P1
2S1
2S2
2S1
2S2
2S1
2S2
2S1
2S2
132 / 33 kV
10 / 16 MVA
MBCH 12
120
240

## Slide 169: Diff. Relay Secondary Wiring
2S1
2S2
2S1
2S2
P1
P1
2S1
2S2
2S1
2S2
2S1
2S2
2S1
2S2
132 / 33 kV
10 / 16 MVA
MBCH 12
120
240

## Slide 170: MBCH 12 Diff Relay connections
120
240

## Slide 171: Differential relay connections
120
240

## Slide 172: PD trip in CB
120
240

## Slide 173: Portable battery charger
120
240

## Slide 174: Portable battery charger
120
240

## Slide 175
Portable battery charger
120
240

## Slide 176: P444 relay – inside -Vermin bite
120
240

## Slide 177: 220 kV Manubolu feeder 3 CB Test results
IR Values G Ω | R | Y | B
In – Out | 966 | 939 | 386
Out – Earth | 3390 | 10000 | 8550
Top – Earth | 10000 | 10000 | 2470
Contact resistance micro Ohms | 55 | 188 / 183 | 50
Timings m Sec |  |  | 
Close | 103 | 122 | 104
TC 1 | 35 | 35 | 37
TC 2 | 36 | 34 | 35
120
240

## Slide 178
RRRV
120
240

## Slide 179
High resistance fault
120
240

## Slide 180
0
120
240